{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":33,"n_cols":6,"rows_kept":33,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","5MXM-A9"]
[]
[]
[]
[]
["","","","","","5MXM90A2V1B9"]
["Dimensions","Unité","","Hauteur","mm","734"]
["","","","Largeur","mm","974"]
["","","","Profondeur","mm","408"]
["Poids","Unité","","","kg","68"]
["Compresseur","Type","","","","Compresseur swing hermétique"]
["Plage de fonctionnement","Rafraîchissement","Temp. ext.","Min.","°CBS","-10"]
["","","","Max.","°CBS","46"]
["Niveau de pression sonore","Rafraîchissement","","Nom.","dBA","52"]
["","Chauffage","","Nom.","dBA","52"]
["Réfrigérant","","","","","R-32"]
["","Charge","","","kg","2.4"]
["","Charge","","","tCO2Eq","1.62"]
["","Réfrigérant-=-PRP","","","","675"]
["Raccords de tuyauterie","Longueur de tuyauterie","Max.","UE - UI","m","25 (1)"]
["","Charge de réfrigérant supplémentaire","","","kg/m","0,02 (pour longueur de tuyauterie supérieure à 30 m)"]
["","Dénivelé","UI - UE","Max.","m","15"]
["","","UI - UI","Max.","m","7.5"]
["","Longueur totale de tuyauterie","Système","Réel","m","75"]
["Accessoires standard","Installation manual","","","","1"]
["","Drain cap","","","","3"]
["","Drain plug","","","","1"]
["","Reducer assembly","","","","1"]
["","Screw bag","","","","1"]
["Alimentation électrique","Phase","","","","1~"]
["","Fréquence","","","Hz","50"]
["","Alimentation électrique-=-Tension-=-V","","","V","220-240"]
["Remarques","","","","","(1) - Par pièce"]