{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":44,"n_cols":10,"rows_kept":44,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAA-DV3P"]
[]
[]
[]
[]
["","","","","","EWAA006D2V3P","EWAA008D2V3P","EWAA011DAV3P","EWAA014DAV3P","EWAA016DAV3P"]
["Puissance frigorifique","Nom.","","","kW","5.83 (1), 5.09 (2)","6.18 (1), 5.44 (2)","11.6 (1), 11.5 (2)","12.8 (1), 12.7 (2)","14.0 (1), 15.3 (2)"]
["Commande de puissance","Méthode","","","","Variable (inverter)","Variable (inverter)","Variable (inverter)","Variable (inverter)","Variable (inverter)"]
["Puissance absorbée","Rafraîchissement","","Nom.","kW","1.08 (1), 1.55 (2)","1.19 (1), 1.73 (2)","3.56 (1), 2.17 (2)","4.06 (1), 2.51 (2)","4.58 (1), 3.24 (2)"]
["EER","","","","","5.40 (1), 3.28 (2)","5.19 (1), 3.14 (2)","3.26 (1), 5.31 (2)","3.16 (1), 5.04 (2)","3.06 (1), 4.74 (2)"]
["SEER","","","","","","","5.79 (5)","5.71 (5)","5.59 (5)"]
["Dimensions","Unité","","Profondeur","mm","362","362","460","460","460"]
["","","","Hauteur","mm","770","770","870","870","870"]
["","","","Largeur","mm","1250","1250","1380","1380","1380"]
["Poids","Unité","","","kg","88","88","147","147","147"]
["Caisson","Couleur","","","","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire"]
["","Matériau","","","","Acier zingué à faible teneur en carbone","Acier zingué à faible teneur en carbone","Tôle d'acier galvanisée et prélaquée polyester","Tôle d'acier galvanisée et prélaquée polyester","Tôle d'acier galvanisée et prélaquée polyester"]
["Échangeur de chaleur air","Type","","","","","","Type de tube et d'ailette à haut rendement avec sous-refroidisseur intégral","Type de tube et d'ailette à haut rendement avec sous-refroidisseur intégral","Type de tube et d'ailette à haut rendement avec sous-refroidisseur intégral"]
["Ventilateur","Quantité","","","","1","1","1","1","1"]
["","Type","","","","Ventilateur à hélice","Ventilateur à hélice","Ventilateur à hélice","Ventilateur à hélice","Ventilateur à hélice"]
["Moteur de ventilateur","Entraînement","","","","","","Entraînement direct","Entraînement direct","Entraînement direct"]
["Compresseur","Quantité","","","","1","1","1","1","1"]
["Compresseur","Type","","","","Compresseur swing hermétique","Compresseur swing hermétique","Compresseur swing hermétique à Inverter","Compresseur swing hermétique à Inverter","Compresseur swing hermétique à Inverter"]
["Compresseur","Méthode de démarrage","","","","","","Commandé par Inverter","Commandé par Inverter","Commandé par Inverter"]
["Plage de fonctionnement","Côté air","Rafraîchissement","Min.","°CBS","10 (3)","10 (3)","10","10","10"]
["","","","Max.","°CBS","43","43","43","43","43"]
["","Côté eau","Évaporateur","Min.","°CBS","5 (3)","5 (3)","5","5","5"]
["","","","Max.","°CBS","22","22","22","22","22"]
["Niveau de puissance sonore","Rafraîchissement","","Nom.","dBA","62","62","67.0","69.0","69.0"]
["Niveau de pression sonore","Rafraîchissement","","Nom.","dBA","49","50","47.7","50.8","51.0"]
["Réfrigérant","","","","","R-32","R-32","R-32","R-32","R-32"]
["","Réfrigérant-=-PRP","","","","675","675","675.0","675.0","675.0"]
["","Charge","","","kg","1.35","1.35"]
["","Circuits","","Quantité","","","","1","1","1"]
["Alimentation électrique","Phase","","","","1~","1~","1~","1~","1~"]
["","Fréquence","","","Hz","50","50","50","50","50"]
["","Alimentation électrique-=-Tension-=-V","","","V","230 +/-10%","230 +/-10%","230","230","230"]
["","Plage de tension","","Min.","%","","","-10","-10","-10"]
["","","","Max.","%","","","10","10","10"]
["Unité","Courant de service","","Max.","A","","","30.8","30.8","30.8"]
["Remarques","","","","","(1) - Condition 1: cooling Ta 35°C - LWE 18°C (DT = 5°C); heating Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(1) - Condition 1: cooling Ta 35°C - LWE 18°C (DT = 5°C); heating Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB"]
["","","","","","(2) - Condition 2: cooling Ta 35°C - LWE 7°C ( DT = 5°C); heating Ta DB/WB 7°C/6°C - LWC 45°C ( DT = 5°C )","(2) - Condition 2: cooling Ta 35°C - LWE 7°C ( DT = 5°C); heating Ta DB/WB 7°C/6°C - LWC 45°C ( DT = 5°C )","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB"]
["","","","","","(3) - Pour en savoir plus, se reporter au schéma de plage de fonctionnement.","(3) - Pour en savoir plus, se reporter au schéma de plage de fonctionnement.","(3) - Conformément à la norme EN14825","(3) - Conformément à la norme EN14825","(3) - Conformément à la norme EN14825"]
["","","","","","","","(4) - En fonction du mode de fonctionnement, voir le manuel d’installation.","(4) - En fonction du mode de fonctionnement, voir le manuel d’installation.","(4) - En fonction du mode de fonctionnement, voir le manuel d’installation."]