{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":43,"n_cols":13,"rows_kept":43,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAD-TZSSC2"]
[]
[]
[]
[]
["","","","","","EWADC16TZSSC2","EWADH19TZSSC2","EWADC15TZSSC2","EWADH17TZSSC2","EWADH13TZSSC2","EWADH11TZSSC2","EWADH12TZSSC2","EWADH18TZSSC2"]
["Puissance frigorifique","Nom.","","","kW","1,644","1,965","1,508","1,766","1,355","1,189","1,259","1,875"]
["Commande de puissance","Méthode","","","","Variable","Variable","Variable","Variable","Variable","Variable","Variable","Variable"]
["","Puissance minimale","","","%","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5"]
["Puissance absorbée","Rafraîchissement","","Nom.","kW","532.8","709.3","485","581.8","438.6","380.9","413.4","636.4"]
["EER","","","","","3.09","2.77","3.11","3.04","3.09","3.12","3.05","2.95"]
["IPLV (valeur intégrée sous charge partielle)","","","","","5.11","4.99","5.14","5.07","4.78","4.85","4.8","5.04"]
["SEER","","","","","4.87","4.68","4.83","4.86","4.65","4.69","4.64","4.83"]
["Dimensions","Unité","","Profondeur","mm","12,302","14,102","11,404","13,202","11,404","10,510","10,510","14,102"]
["","","","Hauteur","mm","2,540","2,540","2,540","2,540","2,540","2,540","2,540","2,540"]
["","","","Largeur","mm","2,282","2,282","2,282","2,282","2,282","2,282","2,282","2,282"]
["Poids","Poids en fonctionnement","","","kg","12,145","13,048","11,727","12,575","11,123","9,879","9,879","13,048"]
["","Unité","","","kg","11,134","12,037","10,716","11,564","10,112","9,322","9,322","12,037"]
["Caisson","Couleur","","","","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire"]
["","Matériau","","","","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte"]
["Échangeur de chaleur air","Type","","","","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal"]
["Ventilateur","Quantité","","","","26","30","24","28","24","22","22","30"]
["","Type","","","","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct"]
["Moteur de ventil.","Entraînement","","","","Marche/arrêt","Marche/arrêt","Marche/arrêt","Marche/arrêt","Marche/arrêt","Marche/arrêt","Marche/arrêt","Marche/arrêt"]
["Compresseur","Quantité_","","","","2","2","2","2","2","2","2","2"]
["","Type","","","","Compresseur monovis commandé par Inverter","Compresseur monovis commandé par Inverter","Compresseur monovis commandé par Inverter","Compresseur monovis commandé par Inverter","Compresseur monovis commandé par Inverter","Compresseur monovis commandé par Inverter","Compresseur monovis commandé par Inverter","Compresseur monovis commandé par Inverter"]
["","Méthode de démarrage","","","","Entraîné par VFD","Entraîné par VFD","Entraîné par VFD","Entraîné par VFD","Entraîné par VFD","Entraîné par VFD","Entraîné par VFD","Entraîné par VFD"]
["Sound power level","Rafraîchissement","","Nom.","dBA","105","107","104","105","104","102","103","106"]
["Niveau de pression sonore","Rafraîchissement","","Nom.","dBA","82","84","81","82","82","80","81","83"]
["Réfrigérant","Type","","","","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a","R-134a"]
["","PRP","","","","1,430","1,430","1,430","1,430","1,430","1,430","1,430","1,430"]
["","Charge","","","kg","220","270","200","250","200","175","175","270"]
["","Circuits","","Quantité","","2","2","2","2","2","2","2","2"]
["Raccords de tuyauterie","Entrée/Sortie d'eau de l'évaporateur (DE)","","","","273","273","273","273","273","219.1","219.1","273"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Fréquence","","","Hz","50","50","50","50","50","50","50","50"]
["","Tension","","","V","400","400","400","400","400","400","400","400"]
["","Plage de tension","","Min.","%","-10","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","%","10","10","10","10","10","10","10","10"]
["Unité","Courant de démarrage","","Max.","A","0","0","0","0","0","0","0","0"]
["","Courant de service","Rafraîch.","Nom.","A","884.0","1,149","813.9","962.8","733.0","646.5","691.1","1,044"]
["","","","Max.","A","1,205","1,487","1,165","1,301","1,027","913","969","1,398"]
["","Courant max. d’unité pour déterminer la taille des fils","","","A","1,326","1,636","1,282","1,431","1,130","1,004","1,066","1,538"]