{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":50,"n_cols":29,"rows_kept":50,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAH-TZXRD"]
[]
[]
[]
[]
["","","","","","EWAH275TZXRD1","EWAH400TZXRD1","EWAH470TZXRD1","EWAH300TZXRD1","EWAH350TZXRD1","EWAH750TZXRD2","EWAH620TZXRD1","EWAH975TZXRD2","EWAH840TZXRD2","EWAHH13TZXRD2","EWAHH11TZXRD2","EWAH545TZXRD2","EWAH220TZXRD1","EWAH540TZXRD1","EWAH645TZXRD2","EWAH465TZXRD2","EWAH600TZXRD2","EWAH515TZXRD1","EWAHH12TZXRD2","EWAH790TZXRD2","EWAH700TZXRD2","EWAH230TZXRD1","EWAH900TZXRD2","EWAHH10TZXRD2"]
["Puissance frigorifique","Nom.","","","kW","271.7","393.5","461.6","295.3","345.2","743.4","607.1","959.8","831.9","1,363","1,167","537.6","216.3","528","632.8","467.2","594.3","497.8","1,257","780.8","687.3","228.3","886","1,066"]
["Commande de puissance","Méthode","","","","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance","À variation continue de puissance"]
["","Puissance minimale","","","%","18","22","19","16","25","12","25","10","11","12","14","10","22","30","14","10","10","17","13","12","13","20","10","10"]
["Puissance absorbée","Rafraîchissement","","Nom.","kW","81.59","122.2","139.1","92.45","98.6","220","194.4","301.6","250.2","419.4","351.2","153.6","68.5","153.8","186.7","132.7","178.3","159.9","384.5","225.2","211.1","75.92","276","327.9"]
["EER","","","","","3.33","3.219","3.319","3.194","3.501","3.379","3.123","3.182","3.325","3.251","3.323","3.494","3.157","3.434","3.389","3.52","3.334","3.112","3.268","3.467","3.255","3.007","3.21","3.251"]
["IPLV (valeur intégrée sous charge partielle)","","","","","6.144","6.619","6.667","6.065","6.641","6.633","5.64","6.445","6.52","6.435","6.498","6.414","6.058","5.796","6.46","6.273","6.301","6.49","6.388","6.648","6.317","6.007","6.407","6.447"]
["SEER","","","","","5.942","6.026","6.284","5.775","6.188","6.392","5.467","6.252","6.318","5.987","5.875","6.133","5.404","5.588","6.207","6.02","6.042","6.103","5.942","6.417","6.095","5.363","6.216","6.226"]
["Dimensions","Unité","","Profondeur","mm","3,760","4,840","5,920","3,760","4,840","8,080","5,920","10,240","9,160","13,480","11,320","7,000","2,680","5,920","7,000","7,000","7,000","5,920","12,400","9,160","7,000","2,680","9,160","11,320"]
["","","","Hauteur","mm","2,553","2,553","2,553","2,553","2,553","2,553","2,553","2,553","2,553","2,553","2,553","2,553","2,553","2,553","2,553","2,553","2,553","2,553","2,553","2,553","2,553","2,553","2,553","2,553"]
["","","","Largeur","mm","2,238","2,238","2,238","2,238","2,238","2,238","2,238","2,238","2,238","2,238","2,238","2,238","2,238","2,238","2,238","2,238","2,238","2,238","2,238","2,238","2,238","2,238","2,238","2,238"]
["Poids","Poids en fonctionnement","","","kg","3,277","4,078","4,634","3,282","4,068","6,256","5,408","7,338","6,748","9,913","8,925","5,180","2,761","5,398","5,504","4,951","5,242","4,639","9,417","6,743","5,509","2,761","6,847","8,241"]
["","Unité","","","kg","3,362","4,143","4,689","3,362","4,143","6,271","5,443","7,323","6,753","9,843","8,880","5,225","2,851","5,443","5,534","5,006","5,277","4,689","9,362","6,753","5,534","2,851","6,842","8,211"]
["Caisson","Couleur","","","","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire","Blanc ivoire"]
["","Matériau","","","","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte","Plaque en acier galvanisé peinte"]
["Échangeur de chaleur-eau / évaporateur","Type","","","","Plaque brasée","Plaque brasée","Plaque brasée","Plaque brasée","Plaque brasée","Multitubulaire - Détente directe","Plaque brasée","Multitubulaire - Détente directe","Multitubulaire - Détente directe","Multitubulaire - Détente directe","Multitubulaire - Détente directe","Multitubulaire - Détente directe","Plaque brasée","Plaque brasée","Multitubulaire - Détente directe","Multitubulaire - Détente directe","Multitubulaire - Détente directe","Plaque brasée","Multitubulaire - Détente directe","Multitubulaire - Détente directe","Multitubulaire - Détente directe","Plaque brasée","Multitubulaire - Détente directe","Multitubulaire - Détente directe"]
["","Volume d'eau","","","l","48","42.7","58.1","48","42.7","492","76.3","583","492","1,011","1,011","232","40","76.3","289","152","289","58.1","1,011","492","289","40","583","1,011"]
["","Chute de pression d'eau","Rafraîchissement","Nom.","kPa","12.7","41.5","31.2","14.9","32.5","46.1","31.2","56.5","54.9","42.4","48.7","33.7","10.2","24","33.2","38.1","30.1","35.9","54.6","49.8","38.6","11.3","49.8","29.2"]
["Échangeur de chaleur air","Type","","","","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal","Microcanal"]
["Ventilateur","Quantité","","","","6","8","10","6","8","14","10","18","16","24","20","12","4","10","12","12","12","10","22","16","12","4","16","20"]
["","Type","","","","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct","Hélice à entraînement direct"]
["","Débit d'air","Rafraîchissement","Nom.","l/s","28,330","37,770","47,213","28,330","37,770","66,098","47,213","84,983","75,540","113,320","94,425","56,660","18,890","47,213","56,660","56,660","56,660","47,213","103,868","75,540","56,660","18,890","75,540","94,425"]
["Moteur de ventilateur","Entraînement","","","","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai","Sans balai"]
["Compresseur","Quantité_","","","","1","1","1","1","1","2","1","2","2","2","2","2","1","1","2","2","2","1","2","2","2","1","2","2"]
["","Type","","","","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis","Compresseur à vis"]
["Plage de fonctionnement","Côté air","Rafraîchissement","Min.","°CBS","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20","-20"]
["","","","Max.","°CBS","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46","46"]
["","Côté eau","Évaporateur","Min.","°CBS","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4","4"]
["","","","Max.","°CBS","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18","18"]
["Niveau de puissance sonore","Rafraîchissement","","Nom.","dBA","89.3","89.4","93.3","89.9","87.9","91","90.2","95.6","92.4","94.2","92.7","90.8","86.7","89.2","89.1","90.5","94.2","91.1","93.4","91.6","90.2","86.9","94.1","94.1"]
["Niveau de pression sonore","Rafraîchissement","","Nom.","dBA","69.6","69.17","72.53","70.14","67.59","69.4","69.5","73.4","70.53","71.07","70.14","69.59","67.62","68.42","67.94","69.38","73.07","70.32","70.59","69.68","69.04","67.78","72.22","71.53"]
["Réfrigérant","Type","","","","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)"]
["","PRP","","","","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7","7"]
["","Charge","","","kg","35","55","65","40","45","105","85","135","115","190","165","75","30","75","90","65","85","70","175","110","95","30","125","150"]
["","Circuits","","Quantité","","1","1","1","1","1","2","1","2","2","2","2","2","1","1","2","2","2","1","2","2","2","1","2","2"]
["Raccords de tuyauterie","Entrée/Sortie d'eau de l'évaporateur (DE)","","","","88.9mm","139.7mm","139.7mm","88.9mm","139.7mm","219.1","139.7mm","219.1","219.1","273","273","168.3mm","88.9mm","139.7mm","168.3mm","139.7mm","168.3mm","139.7mm","273","219.1","168.3mm","88.9mm","219.1","273"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Fréquence","","","Hz","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50"]
["","Tension","","","V","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400"]
["","Plage de tension","","Min.","%","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","%","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10","10"]
["Unité","Courant de démarrage","","Max.","A","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["","Courant de service","Rafraîch.","Nom.","A","180.6","249.8","283.6","199.6","216.9","454.5","366.7","592.9","507.6","793.9","675.5","343.5","150.2","306.1","401.1","305.9","386.6","314.9","732.6","470","433.8","163.3","547.1","642.8"]
["","","","Max.","A","214","310","357","236","269","527","491","702","618","1,090","902","406","172","414","472","364","448","394","992","579","517","183","655","787"]
["","Courant max. d’unité pour déterminer la taille des fils","","","A","235.2","340.5","392.5","259.2","296.4","580.1","540.6","772.2","679.6","1,198.5","992","442.5","189.5","455.7","519.6","400.6","492.4","433.7","1,091.3","636.9","568.6","201","720.6","866"]