{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":70,"n_cols":11,"rows_kept":70,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWXT-ATV3C"]
[]
[]
[]
[]
["","","","","","FWXT10ABTV3C","FWXT10AATV3C","FWXT15ABTV3C","FWXT15AATV3C","FWXT20ABTV3C","FWXT20AATV3C"]
["Puissance frigorifique","7/12°C","","Min.","kW","0.49","0.48","0.62","0.58","0.70","0.91"]
["","","","Moy.","kW","0.88","0.80","1.08","1.03","1.21","1.75"]
["","","","Max.","kW","1.24","1.07","1.61","1.65","1.94","2.31"]
["Puissance frigorifique sensible","7/12°C","","Min.","kW","0.37","0.39","0.52","0.49","0.57","0.76"]
["","","","Moy.","kW","0.70","0.69","0.86","0.91","1.02","1.53"]
["","","","Max.","kW","0.98","0.95","1.27","1.49","1.52","1.94"]
["Puissance calorifique","45/40°C","","Min.","kW","0.55","0.53","0.79","0.66","0.74","0.96"]
["","","","Moy.","kW","1.00","0.94","1.36","1.26","1.55","1.98"]
["","","","Max.","kW","1.50","1.27","2.01","1.80","2.13","2.60"]
["Puissance absorbée","Min.","","","kW","0.01","0","0.01","0.01","0.01","0.01"]
["","Moy.","","","kW","0.01","","0.01","","0.01"]
["","Max.","","","kW","0.02","0.01","0.02","0.01","0.03","0.02"]
["Vitesse de ventilation","Min.","","","tr/min","680.00","84.00","680.00","124.00","680.00","138.00"]
["","Moy.","","","tr/min","1100.00","155.00","1100.00","229.00","1100.00","283.00"]
["","Max.","","","tr/min","1500.00","228.00","1500.00","331.00","1500.00","440.00"]
["Caisson","Couleur","","","","RAL 9003","RAL 9003","RAL 9003","RAL 9003","RAL 9003","RAL 9003"]
["","Matériau","","","","Tôle","Tôle","Tôle","Tôle","Tôle","Tôle"]
["Dimensions","Unité","","Hauteur","mm","335","335","335","335","335","335"]
["","","","Largeur","mm","902","902","1102","1100","1302","1300"]
["","","","Profondeur","mm","128","128","128","128","128","128"]
["","Unité emballée","","Hauteur","mm","490","490","490","490","490","490"]
["","","","Largeur","mm","1030","1030","1230","1230","1430","1430"]
["","","","Profondeur","mm","210","210","210","210","210","210"]
["Poids","Unité","","","kg","14","14","16","16","19","19"]
["","Unité emballée","","","kg","15","15","17","17","20","20"]
["Emballage","Matériau","","","","Carton","Carton","Carton","Carton","Carton","Carton"]
["","Poids","","","kg","1","1","1","1","1","1"]
["Échangeur de chaleur","Quantité","","","","1","1","1","1","1","1"]
["","Volume interne de serpentin","","","L","0.5","0.5","0.61","0.7","0.77","0.9"]
["","Charge","","Pression de service","bars","10","","10","","10"]
["Circuit d'eau","Diamètre des raccords de tuyauterie","","","in","3/4","3/4","3/4","3/4","3/4","3/4"]
["","Matériau de tuyauterie","","","","CUIVRE","Laiton (CW617N)","CUIVRE","Laiton (CW617N)","CUIVRE","Laiton (CW617N)"]
["","Pression","Chauffage","Max.","bars","10","10","10","10","10","10"]
["Circuit d’eau - chute de pression d’eau","Chauffage","45/40°C","Min.","kPa","5.10","1.10","4.81","2.80","6.00","1.10"]
["","","","Moy.","kPa","12.00","3.10","6.30","3.50","6.40","4.10"]
["","","","Max.","kPa","16.30","5.40","7.20","4.00","8.10","6.60"]
["","Rafraîchissement","7/12°C","Min.","kPa","4.80","1.10","4.70","3.90","5.50","1.30"]
["","","","Moy.","kPa","10.50","3.00","5.60","4.80","5.40","4.20"]
["","","","Max.","kPa","11.70","5.20","5.10","5.70","5.30","6.90"]
["Circuit d’eau - débit d’eau","Chauffage","45/40°C","Min.","kg/h","100.00","91.90","140","112.60","150.00","164.80"]
["","","","Moy.","kg/h","170.00","162.00","240","216.60","300.00","341.00"]
["","","","Max.","kg/h","260.00","218.40","350","310.00","420.00","447.20"]
["","Rafraîchissement","7/12°C","Circuit d’eau - débit d’eau-=-Rafraîchissement-=-7/12°C-=-Min.-=-kg/h","kg/h","80.00","82.10","110","98.90","120.00","156.50"]
["","","","Moy.","kg/h","150.00","138.10","190","177.40","210.00","300.60"]
["","","","Max.","kg/h","210.00","184.40","280","283.00","330.00","396.80"]
["Niveau de puissance sonore","Min.","","","dBA","35","34","36","34","37","35"]
["","Moy.","","","dBA","46","","47","","48"]
["Niveau de puiss. sonore","Max.","","","dBA","53.0","49.0","54.0","51.0","55.0","52.0"]
["Plage de fonctionnement","Chauffage","Côté eau","Min.","°C","30","30","30","30","30","30"]
["","","","Max.","°C","85","85","85","85","85","85"]
["","Rafraîchissement","Côté eau","Min.","°C","5","5","5","5","5","5"]
["","","","Max.","°C","18","18","18","18","18","18"]
["","Installation des unités intérieures","Temp. ext.","Min.","°CBS","0","0","0","0","0","0"]
["","","","Max.","°CBS","45","45","45","45","45","45"]
["Systèmes de commande","Télécommande infrarouge","","","","Pour FWXT-ATV3(C)(CL)","","Pour FWXT-ATV3(C)(CL)","","Pour FWXT-ATV3(C)(CL)"]
["","Intégré sur l'unité intérieure","","","","Oui","Non","Oui","Non","Oui","Non"]
["Alimentation électrique","Phase","","","","1~","1~","1~","1~","1~","1~"]
["","Fréquence","","","Hz","50","50","50","50","50","50"]
["","Alimentation électrique-=-Tension-=-V","","","V","230","230","230","230","230","230"]
["Consommation électrique","Max.","","","W","19","18","20","20","29","27"]
["","Veille","","","W","3","5","4","5","5","6"]
["Courant","Courant de fonctionnement maximum","","Chauffage","A","0.16","0.2","0.18","0.2","0.24","0.2"]
["","Courant de service max.","","Rafraîch.","A","0.16","0.2","0.18","0.2","0.24","0.2"]
["Échangeur de chaleur","Charge","","Échangeur de chaleur-=-Charge-=-Pression de service-=-bar","bars","","10","","10","","10"]