{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":20,"n_cols":9,"rows_kept":20,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","VH-B"]
[]
[]
[]
[]
["","","","VH1B","VH2B","VH3B","VH4/AB","VH4B","VH5B"]
["Courant de sortie (maximum)","","","19 A à 40 °C (température extérieure)","19 A à 40 °C (température extérieure)","19 A à 40 °C (température extérieure)","19 A à 40 °C (température extérieure)","19 A à 40 °C (température extérieure)","19 A à 40 °C (température extérieure)"]
["Unité connectable","","","VAM150FA","VAM250FA, VAM350FB","VAM500FB, VAM650FB","VAM800FB, VAM1000FB","VAM800FB, VAM1000FB","VAM1500FB, VAM2000FB"]
["Témoins LED","","","Sous tension - Jaune, Dispositif de chauffage activé - Rouge (fixe ou clignotant, indication d'une commande à impulsion), Erreur de débit d'air - Rouge","Sous tension - Jaune, Dispositif de chauffage activé - Rouge (fixe ou clignotant, indication d'une commande à impulsion), Erreur de débit d'air - Rouge","Sous tension - Jaune, Dispositif de chauffage activé - Rouge (fixe ou clignotant, indication d'une commande à impulsion), Erreur de débit d'air - Rouge","Sous tension - Jaune, Dispositif de chauffage activé - Rouge (fixe ou clignotant, indication d'une commande à impulsion), Erreur de débit d'air - Rouge","Sous tension - Jaune, Dispositif de chauffage activé - Rouge (fixe ou clignotant, indication d'une commande à impulsion), Erreur de débit d'air - Rouge","Sous tension - Jaune, Dispositif de chauffage activé - Rouge (fixe ou clignotant, indication d'une commande à impulsion), Erreur de débit d'air - Rouge"]
["Relais de fonctionnement","","","1 A 120 Vca ou 1 A 24 Vcc","1 A 120 Vca ou 1 A 24 Vcc","1 A 120 Vca ou 1 A 24 Vcc","1 A 120 Vca ou 1 A 24 Vcc","1 A 120 Vca ou 1 A 24 Vcc","1 A 120 Vca ou 1 A 24 Vcc"]
["Diamètre de gaine","mm","","100","150","200","250","250","350"]
["Puissance","kW","","1.0","1.0","1.0","2.5","1.5","2.5"]
["Trous de montage","","","Centres 98mm x 181mm, orifices 5mm Ø","Centres 98mm x 181mm, orifices 5mm Ø","Centres 98mm x 181mm, orifices 5mm Ø","Centres 98mm x 181mm, orifices 5mm Ø","Centres 98mm x 181mm, orifices 5mm Ø","98 mm x 181 mm centres trous de 5 mm"]
["Température ambiante maximale à proximité de la boîte à bornes","","","35 °C (pendant le fonctionnement)","35 °C (pendant le fonctionnement)","35 °C (pendant le fonctionnement)","35 °C (pendant le fonctionnement)","35 °C (pendant le fonctionnement)","35 °C (pendant le fonctionnement)"]
["Capteur de température","","","5 kOhms à 25 °C (tableau 502 1T)","5 kOhms à 25 °C (tableau 502 1T)","5 kOhms à 25 °C (tableau 502 1T)","5 kOhms à 25 °C (tableau 502 1T)","5 kOhms à 25 °C (tableau 502 1T)","5 kOhms à 25 °C (tableau 502 1T)"]
["Entrée de consigne de GTB","","","0-10 Vcc","0-10 Vcc","0-10 Vcc","0-10 Vcc","0-10 Vcc","0-10 Vcc"]
["Plage de commande de température","","","De 0 à 40 °C / (0-10 V 0-100 %)","De 0 à 40 °C / (0-10 V 0-100 %)","De 0 à 40 °C / (0-10 V 0-100 %)","De 0 à 40 °C / (0-10 V 0-100 %)","De 0 à 40 °C / (0-10 V 0-100 %)","De 0 à 40 °C / (0-10 V 0-100 %)"]
["Fusible de commande","","","20 x 5mm 250 mA","20 x 5mm 250 mA","20 x 5mm 250 mA","20 x 5mm 250 mA","20 x 5mm 250 mA","20 x 5mm 250 mA"]
["Power supply","Fréquence","Hz","50/60","50/60","50/60","50/60","50/60","50/60"]
["","Tension","V","220/250","220/250","220/250","220/250","220/250","220/250"]